protect / Miniature circuit-breaker (MCB)

Circuit-breakers, C-characteristic, 25 A/230 V, 400 V AC, 25 A/60 V DC, 6 kA, for commercial sector applications

Miniature circuit-breakers (MCBs) of type DLS 6 are predominately used for overcurrent protection of cables and lines as per VDE 0100-430 and protection against electrical shock as per VDE 0100-410.
Devices of the h design for workshops are fitted with a high rated switching capacity of 6 kA for residential applications and provide screw terminals with top and bottom strain-relief clamps.
 special quick fastening for removal of multiple miniature circuit-breakers from the bottom or top interconnection
 large, folding label window for a secure hold and protection of the label
 use of conventional wiring rails
 ON/OFF switch position indicator on the switch toggle
 accessories retro-fittable on the right
 labelling software free of charge
 
Tripping characteristic: C
Number of poles: 1
Insulation group (250 V AC): C
Isolation class (400 V AC): B

load circuit (load disconnect contact):
1 NO
Number of poles (total): 1
Rated voltage (AC): 230 V, 400 V
Rated current AC (typ.): 25 A 
Rated frequency: 50 Hz (16.67 Hz ... 60 Hz)
Rated voltage (DC): 60 V
Rated current DC (typ.): 25 A
Rated insulation voltage: 2 kV
Rated switching capacity as of EN 60898 at 230 V: 6 kA
Rated switching capacity as of EN 60898 at 400 V: 6 kA

screw terminals with strain-relief clamp top (load circuit):
Cross section solid: 1-wire: 0.5 mm² ... 25 mm²
Cross section stranded: 1-wire: 1.5 mm² ... 25 mm²
Connecting capacity flexible: 1-wire: 1 mm² ... 16 mm²
Cross section flexible with ferrule: 0.5 mm² ... 16 mm²

screw terminals with strain-relief clamp bottom (load circuit):
Cross section solid: 1-wire: 0.5 mm² ... 35 mm²
Cross section stranded: 1-wire: 1.5 mm² ... 35 mm²
Connecting capacity flexible: 1-wire: 1 mm² ... 25 mm²
Cross section flexible with ferrule: 0.5 mm² ... 16 mm²

 Ambient temperature: min. -25 °C ... max. 55 °C

Housing type: distribution board housing
Installation type: Mounting rail (35 mm)
Protection class: IP20
Dimensions of transformer opening: W 17.7 mm (1 MW (module width)) × H 82.5 mm × D 74 mm

Certifications: VDE
Design requirements/Standards: EN 60898-1, VDE 0641-11

Factory: Doepke or similar
Item designation: DLS 6h C25-1
Order number: 09914205
selected make/type: ___________/___________